## Sheet1
Estimated Average Engine Performance NOT FOR GUARANTEE, REFER TO PROJECT F&ID FOR DESIGN
GE Energy
2010-01-13
Performance By: | Perez, Monica | [10 empty] | 2010-03-14 | 2010-02-12
Project Info: | AUSTIN-TX FROM 5 TO 110 F (TAMB) DLE
Engine: | LM2500+ G4 6 Stage DLE (RD) w/o Flow Enhancer
Deck Info: | GE166B - 8aj.scp | [5 empty] | Date: | 11/18/2009
Generator: | BDAX 71-193ER 60Hz, 13.8kV, 0.85PF (16294) | [5 empty] | Time: | 4:46:40 PM
Fuel: | Gas Fuel #10-1, 19000 Btu/lb,LHV | [5 empty] | Version: | 3.8.5
Case # | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121
Ambient Conditions
Dry Bulb, °F | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110
Wet Bulb, °F | 3.5 | 8.1 | 12.7 | 17.3 | 21.8 | 26.2 | 30.5 | 34.9 | 39.2 | 43.6 | 47.9 | 52.3 | 56.6 | 60.9 | 65.2 | 69.6 | 73.9 | 78.3 | 82.7 | 87 | 91.4 | 95.8
RH, % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Altitude, ft | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530
Ambient Pressure, psia | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417 | 14.417
Engine Inlet
Comp Inlet Temp, °F | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110
RH, % | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Conditioning | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE | NONE
Tons or kBtu/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pressure Losses
Inlet Loss, inH20 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Exhaust Loss, inH20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Partload % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
kW, Gen Terms | 34411 | 34526 | 34635 | 34736 | 34830 | 34812 | 34313 | 33663 | 32946 | 32334 | 31746 | 31170 | 30607 | 29997 | 29236 | 28472 | 27645 | 26836 | 26032 | 25217 | 24444 | 23712
Est. Btu/kW-hr, LHV | 8766 | 8779 | 8792 | 8805 | 8817 | 8831 | 8849 | 8881 | 8921 | 8955 | 8987 | 9020 | 9054 | 9094 | 9153 | 9217 | 9291 | 9370 | 9455 | 9550 | 9646 | 9745
Guar. Btu/kW-hr, LHV | 8945 | 8958 | 8971 | 8984 | 8997 | 8965 | 8984 | 9016 | 9057 | 9092 | 9124 | 9158 | 9192 | 9232 | 9293 | 9358 | 9432 | 9513 | 9599 | 9695 | 9793 | 9893
Fuel Flow
MMBtu/hr, LHV | 301.7 | 303.1 | 304.5 | 305.8 | 307.1 | 307.4 | 303.6 | 299 | 293.9 | 289.6 | 285.3 | 281.2 | 277.1 | 272.8 | 267.6 | 262.4 | 256.8 | 251.4 | 246.1 | 240.8 | 235.8 | 231.1
lb/hr | 15877 | 15953 | 16026 | 16097 | 16163 | 16180 | 15981 | 15735 | 15470 | 15240 | 15016 | 14798 | 14585 | 14358 | 14085 | 13813 | 13518 | 13234 | 12954 | 12675 | 12410 | 12161
NOx Control | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE | DLE
Control Parameters
HP Speed, RPM | 9522 | 9573 | 9624 | 9674 | 9725 | 9764 | 9752 | 9720 | 9690 | 9713 | 9736 | 9759 | 9784 | 9809 | 9834 | 9859 | 9881 | 9904 | 9928 | 9950 | 9974 | 10001
PT Speed, RPM | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
PS3 - CDP, psia | 357 | 356.6 | 356.2 | 355.7 | 355.2 | 354.1 | 350.6 | 345.9 | 340.6 | 336.3 | 332.1 | 328 | 323.9 | 319.5 | 314 | 308.4 | 302.2 | 296.2 | 290.1 | 284.1 | 278.3 | 272.8
T3CRF - CDT, °F | 845.8 | 858 | 870.1 | 882.1 | 893.9 | 904.1 | 907.4 | 909.8 | 912.1 | 916.1 | 920 | 923.9 | 927.7 | 931.5 | 934.9 | 938.1 | 940.8 | 943.4 | 945.8 | 948.1 | 950.2 | 952.3
T48IN, °R | 1932 | 1949 | 1965 | 1982 | 1998 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011
T48IN, °F | 1472 | 1489 | 1506 | 1522 | 1538 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551 | 1551
Exhaust Parameters
Temperature, °F | 907 | 920.3 | 933.5 | 946.6 | 959.4 | 970.4 | 973.3 | 977 | 981.2 | 985 | 988.6 | 992.3 | 996 | 1000.1 | 1005.3 | 1010.7 | 1016.5 | 1022.6 | 1028.9 | 1035.6 | 1042.1 | 1048.8
lb/sec | 215.2 | 214.1 | 213 | 211.9 | 210.8 | 209.5 | 207.4 | 204.8 | 201.8 | 199.3 | 196.8 | 194.3 | 191.9 | 189.2 | 185.9 | 182.5 | 178.8 | 175.1 | 171.5 | 167.8 | 164.2 | 160.7
lb/hr | 774884 | 770808 | 766761 | 762734 | 758718 | 754122 | 746731 | 737152 | 726497 | 717315 | 708317 | 699485 | 690686 | 681095 | 669121 | 657003 | 643625 | 630483 | 617336 | 603964 | 591097 | 578642
Energy, Btu/s- Ref 0 °R | 74414 | 74832 | 75244 | 75645 | 76029 | 76242 | 75685 | 74949 | 74136 | 73451 | 72778 | 72128 | 71491 | 70796 | 69916 | 69037 | 68049 | 67105 | 66177 | 65251 | 64379 | 63573
Cp, Btu/lb-R | 0.2715 | 0.2721 | 0.2727 | 0.2734 | 0.274 | 0.2746 | 0.2748 | 0.275 | 0.2753 | 0.2756 | 0.2759 | 0.2763 | 0.2767 | 0.2772 | 0.2778 | 0.2785 | 0.2792 | 0.2801 | 0.2811 | 0.2822 | 0.2835 | 0.2849
Emissions (ESTIMATED, NOT FOR GUARANTEE)
NOx ppmvd Ref 15% O2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
NOx as NO2, lb/hr | 30.46 | 30.61 | 30.75 | 30.89 | 31.02 | 31.06 | 30.68 | 30.2 | 29.69 | 29.25 | 28.82 | 28.4 | 27.99 | 27.56 | 27.03 | 26.51 | 25.95 | 25.4 | 24.87 | 24.33 | 23.82 | 23.35
CO ppmvd Ref 15% O2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
CO, lb/hr | 18.54 | 18.63 | 18.72 | 18.8 | 18.88 | 18.91 | 18.67 | 18.38 | 18.07 | 17.81 | 17.54 | 17.29 | 17.04 | 16.77 | 16.46 | 16.14 | 15.79 | 15.46 | 15.14 | 14.81 | 14.5 | 14.21
CO2, lb/hr | 40129.32 | 40317.29 | 40499.97 | 40674.68 | 40837.7 | 40878.16 | 40375.57 | 39755.52 | 39086.2 | 38505.36 | 37939.48 | 37390.3 | 36851.94 | 36277.5 | 35587.52 | 34900.43 | 34155.65 | 33437.13 | 32729.42 | 32021.71 | 31351.23 | 30722.7
HC ppmvd Ref 15% O2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
HC, lb/hr | 6.27 | 6.3 | 6.33 | 6.36 | 6.39 | 6.4 | 6.32 | 6.22 | 6.11 | 6.02 | 5.93 | 5.85 | 5.76 | 5.67 | 5.57 | 5.46 | 5.34 | 5.23 | 5.12 | 5.01 | 4.91 | 4.81
SOX as SO2, lb/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exh Wght % Wet (NOT FOR USE IN ENVIRONMENTAL PERMITS)
AR | 1.2607 | 1.2602 | 1.2597 | 1.2591 | 1.2584 | 1.2577 | 1.2572 | 1.2565 | 1.2558 | 1.2548 | 1.2537 | 1.2524 | 1.2508 | 1.249 | 1.2468 | 1.2443 | 1.2414 | 1.238 | 1.2341 | 1.2296 | 1.2244 | 1.2185
N2 | 74.1009 | 74.0736 | 74.0434 | 74.0099 | 73.9725 | 73.9332 | 73.902 | 73.864 | 73.818 | 73.7626 | 73.6966 | 73.6183 | 73.5258 | 73.4173 | 73.2902 | 73.1422 | 72.9706 | 72.7719 | 72.5429 | 72.2797 | 71.978 | 71.6328
O2 | 15.4702 | 15.3888 | 15.307 | 15.2251 | 15.1435 | 15.0776 | 15.0872 | 15.0951 | 15.0993 | 15.0994 | 15.0956 | 15.0869 | 15.0723 | 15.0519 | 15.0239 | 14.9876 | 14.9423 | 14.886 | 14.818 | 14.7368 | 14.6413 | 14.5274
CO2 | 5.1787 | 5.2305 | 5.282 | 5.3327 | 5.3825 | 5.4206 | 5.407 | 5.3931 | 5.3801 | 5.368 | 5.3563 | 5.3454 | 5.3356 | 5.3264 | 5.3185 | 5.3121 | 5.3068 | 5.3034 | 5.3017 | 5.3019 | 5.3039 | 5.3094
H20 | 3.9836 | 4.0409 | 4.1019 | 4.1671 | 4.237 | 4.3047 | 4.3405 | 4.3851 | 4.4407 | 4.5091 | 4.5917 | 4.691 | 4.8094 | 4.9494 | 5.1145 | 5.3078 | 5.533 | 5.7947 | 6.0973 | 6.446 | 6.8463 | 7.3057
SO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO | 0.0024 | 0.0024 | 0.0024 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025
HC | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008 | 0.0008
NOX | 0.0027 | 0.0027 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028 | 0.0028
Exh Mole % Dry (NOT FOR USE IN ENVIRONMENTAL PERMITS)
AR | 0.9627 | 0.963 | 0.9633 | 0.9637 | 0.964 | 0.9642 | 0.9641 | 0.9641 | 0.964 | 0.964 | 0.9639 | 0.9639 | 0.9639 | 0.9639 | 0.9639 | 0.9639 | 0.9639 | 0.964 | 0.9641 | 0.9642 | 0.9644 | 0.9645
N2 | 80.692 | 80.7202 | 80.7484 | 80.7763 | 80.804 | 80.8256 | 80.8196 | 80.8138 | 80.8087 | 80.8044 | 80.8007 | 80.798 | 80.7963 | 80.7956 | 80.7964 | 80.7986 | 80.8025 | 80.8084 | 80.8165 | 80.827 | 80.84 | 80.8569
O2 | 14.7487 | 14.6817 | 14.6147 | 14.5481 | 14.4824 | 14.4309 | 14.4451 | 14.4591 | 14.4712 | 14.4814 | 14.4901 | 14.4966 | 14.5005 | 14.5022 | 14.5004 | 14.495 | 14.4859 | 14.4718 | 14.4526 | 14.4276 | 14.3965 | 14.3564
CO2 | 3.5898 | 3.6283 | 3.6667 | 3.7049 | 3.7426 | 3.7722 | 3.764 | 3.756 | 3.749 | 3.7432 | 3.7382 | 3.7345 | 3.7322 | 3.7312 | 3.7323 | 3.7354 | 3.7406 | 3.7487 | 3.7597 | 3.774 | 3.7919 | 3.8149
H20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO | 0.0026 | 0.0026 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0028 | 0.0028
HC | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0017 | 0.0017
NOX | 0.0026 | 0.0026 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0028 | 0.0028
Exh Mole % Wet (NOT FOR USE IN ENVIRONMENTAL PERMITS)
AR | 0.9019 | 0.9013 | 0.9007 | 0.9 | 0.8992 | 0.8985 | 0.8979 | 0.8971 | 0.8963 | 0.8952 | 0.8939 | 0.8924 | 0.8907 | 0.8886 | 0.8862 | 0.8834 | 0.8801 | 0.8763 | 0.872 | 0.867 | 0.8614 | 0.8549
N2 | 75.5928 | 75.547 | 75.4966 | 75.4408 | 75.3788 | 75.3141 | 75.2641 | 75.2032 | 75.1293 | 75.0404 | 74.9344 | 74.8087 | 74.6604 | 74.4866 | 74.2834 | 74.0472 | 73.7737 | 73.4581 | 73.0954 | 72.6802 | 72.2063 | 71.6667
O2 | 13.8167 | 13.7407 | 13.6642 | 13.5871 | 13.51 | 13.4468 | 13.4522 | 13.4552 | 13.4542 | 13.4484 | 13.438 | 13.422 | 13.3993 | 13.3698 | 13.3316 | 13.2838 | 13.2258 | 13.1554 | 13.0718 | 12.9734 | 12.859 | 12.7246
CO2 | 3.3629 | 3.3957 | 3.4282 | 3.4602 | 3.4913 | 3.515 | 3.5053 | 3.4952 | 3.4855 | 3.4762 | 3.4668 | 3.4576 | 3.4488 | 3.4399 | 3.4314 | 3.4232 | 3.4152 | 3.4077 | 3.4005 | 3.3936 | 3.3869 | 3.3813
H20 | 6.3194 | 6.4088 | 6.5038 | 6.6053 | 6.714 | 6.819 | 6.874 | 6.9426 | 7.0281 | 7.1333 | 7.2602 | 7.4126 | 7.5943 | 7.8086 | 8.0609 | 8.3559 | 8.6987 | 9.096 | 9.5538 | 10.0793 | 10.68 | 11.3661
SO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO | 0.0024 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0026 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025
HC | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.0015
NOX | 0.0024 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0026 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025
Aero Energy Fuel Number | 10-1 (GEDEF) | [10 empty] | 10-1 (GEDEF)
| Volume % | Weight % | [9 empty] | Volume % | Weight %
Hydrogen | 0 | 0 | [9 empty] | 0 | 0
Methane | 84.5 | 71.8447 | [9 empty] | 84.5 | 71.8447
Ethane | 5.58 | 8.8924 | [9 empty] | 5.58 | 8.8924
Ethylene | 0 | 0 | [9 empty] | 0 | 0
Propane | 2.05 | 4.7909 | [9 empty] | 2.05 | 4.7909
Propylene | 0 | 0 | [9 empty] | 0 | 0
Butane | 0.78 | 2.4027 | [9 empty] | 0.78 | 2.4027
Butylene | 0 | 0 | [9 empty] | 0 | 0
Butadiene | 0 | 0 | [9 empty] | 0 | 0
Pentane | 0.18 | 0.6883 | [9 empty] | 0.18 | 0.6883
Cyclopentane | 0 | 0 | [9 empty] | 0 | 0
Hexane | 0.17 | 0.7764 | [9 empty] | 0.17 | 0.7764
Heptane | 0 | 0 | [9 empty] | 0 | 0
Carbon Monoxide | 0 | 0 | [9 empty] | 0 | 0
Carbon Dioxide | 0.67 | 1.5628 | [9 empty] | 0.67 | 1.5628
Nitrogen | 5.93 | 8.8044 | [9 empty] | 5.93 | 8.8044
Water Vapor | 0 | 0 | [9 empty] | 0 | 0
Oxygen | 0.14 | 0.2374 | [9 empty] | 0.14 | 0.2374
Hydrogen Sulfide | 0 | 0 | [9 empty] | 0 | 0
Ammonia | 0 | 0 | [9 empty] | 0 | 0
Btu/lb, LHV | 19000 | [10 empty] | 19000
Btu/scf, LHV | 946 | [10 empty] | 946
Btu/scf, HHV | 1047 | [10 empty] | 1047
Btu/lb, HHV | 20996 | [10 empty] | 20996
Fuel Temp, °F | 77 | [10 empty] | 77
NOx Scalar | 0.998 | [10 empty] | 0.998
Specific Gravity | 0.65 | [10 empty] | 0.65
Wobbe | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657 | 50.657
Engine Exhaust
Exhaust Avg. Mol. Wt., Wet Basis | 28.6 | 28.6 | 28.6 | 28.6 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.4 | 28.4 | 28.4 | 28.4 | 28.3 | 28.3 | 28.2 | 28.2 | 28.1 | 28
Exhaust Flow, ACFM | 448220 | 450306 | 452349 | 454322 | 456182 | 457077 | 453634 | 449094 | 444064 | 439805 | 435605 | 431526 | 427504 | 423110 | 417565 | 411994 | 405744 | 399714 | 393749 | 387756 | 382050 | 376696
Exhaust Flow, SCFM | 165514 | 164683 | 163861 | 163047 | 162239 | 161310 | 159767 | 157764 | 155540 | 153641 | 151792 | 149992 | 148213 | 146279 | 143851 | 141411 | 138718 | 136098 | 133500 | 130878 | 128392 | 126026
Exhaust Flow, Btu/lb | 346 | 349 | 353 | 357 | 361 | 364 | 365 | 366 | 367 | 369 | 370 | 371 | 373 | 374 | 376 | 378 | 381 | 383 | 386 | 389 | 392 | 396
Exhaust Flow, Calories/s | 18752330 | 18857575 | 18961407 | 19062579 | 19159253 | 19213045 | 19072646 | 18887256 | 18682215 | 18509764 | 18340060 | 18176230 | 18015618 | 17840474 | 17618846 | 17397294 | 17148446 | 16910373 | 16676492 | 16443161 | 16223384 | 16020518
Inlet Flow Wet, pps | 212.9 | 211.7 | 210.6 | 209.4 | 208.3 | 207 | 205 | 202.4 | 199.4 | 196.9 | 194.5 | 192.1 | 189.7 | 187 | 183.8 | 180.4 | 176.8 | 173.2 | 169.6 | 165.9 | 162.4 | 158.9
Inlet Flow Dry, pps | 212.8 | 211.6 | 210.4 | 209.1 | 207.9 | 206.5 | 204.4 | 201.7 | 198.7 | 196 | 193.4 | 190.8 | 188.2 | 185.3 | 181.7 | 178 | 174 | 170 | 165.9 | 161.6 | 157.5 | 153.4
Shaft HP | 47193 | 47351 | 47501 | 47640 | 47768 | 47743 | 47059 | 46173 | 45194 | 44358 | 43556 | 42775 | 42007 | 41174 | 40137 | 39097 | 37972 | 36872 | 35779 | 34670 | 33621 | 32624
Generator Information
Capacity kW | 54086 | 53474 | 52815 | 52115 | 51376 | 50602 | 49797 | 48961 | 48098 | 47209 | 46295 | 45357 | 44394 | 43407 | 42396 | 41358 | 40292 | 39197 | 38069 | 36907 | 35706 | 34463
Efficiency | 0.9778 | 0.9778 | 0.9778 | 0.9778 | 0.9778 | 0.9778 | 0.9778 | 0.9777 | 0.9776 | 0.9775 | 0.9774 | 0.9772 | 0.9771 | 0.977 | 0.9768 | 0.9766 | 0.9763 | 0.976 | 0.9757 | 0.9754 | 0.975 | 0.9747
Inlet Temp, °F | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110
Gear Box Loss | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Burner Mode | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC | ABC
8th Stage Bleed
Flow, pps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pressure, psia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temperature, °R | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CDP Bleed
Flow, pps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pressure, psia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WAR36 - Combustor Water to Air Ratio | 0.0007 | 0.0009 | 0.0011 | 0.0014 | 0.0017 | 0.0021 | 0.0026 | 0.0032 | 0.0038 | 0.0046 | 0.0056 | 0.0067 | 0.008 | 0.0095 | 0.0113 | 0.0134 | 0.0158 | 0.0186 | 0.0218 | 0.0255 | 0.0298 | 0.0348
WA36 - Combustor Air Flow
WF36 - Combustor Fuel Flow
WFA - Fuel Flow, A Ring | 7030.69 | 7000.28 | 7090.86 | 7180.47 | 7268.78 | 7335.07 | 7300.43 | 7234.54 | 7157.02 | 7112.35 | 7068.84 | 7026.9 | 6985.4 | 6935.84 | 6858.92 | 6778.83 | 6682.32 | 6588.07 | 6471.9 | 6350.06 | 6236.61 | 6130.62
WFB - Fuel Flow, B Ring | 6393.22 | 6541.08 | 6557.71 | 6571.52 | 6581.3 | 6562.87 | 6423.46 | 6274.47 | 6120.53 | 5965.68 | 5814.58 | 5667.58 | 5523.83 | 5375.67 | 5215.65 | 5059.63 | 4899.97 | 4747.07 | 4619.52 | 4497.34 | 4379.12 | 4267.98
WFC - Fuel Flow, C Ring | 2452.81 | 2411.23 | 2377.77 | 2344.92 | 2312.74 | 2281.97 | 2256.8 | 2225.98 | 2192.29 | 2161.7 | 2132.18 | 2103.65 | 2075.75 | 2046.09 | 2009.99 | 1974.27 | 1935.84 | 1898.85 | 1862.78 | 1827.11 | 1793.88 | 1762.83
CardPack | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj | 8aj
NSI | 302 | 302 | 302 | 302 | 302 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317
NSI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1305 | 1305
NSI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0